Name:

Course and Year: BEET 3 C

Self Evaluation

- How are standard sectional switch (device) boxes mounted?

- An offset bar hanger is a device on which boxes are fastened so they can be mounted between joists or studs. The hangers are available in adjusting types for different joist spacings.

- What is an offset bar hanger?

- An offset bar hanger is a device on which boxes are fastened so they can be mounted between joists or studs. The hangers are available in adjusting types for different joist spacings.

- What types of boxes may be used with offset bar hangers?

- Practically any outlet or switch box which has a trade size in. knockout can be used with offset bar hangers.

- What methods may be used to mount luminaires to an outlet box fastened to an offset bar hanger?

- Luminaires are mounted to an outlet box using a luminaire stud or No. 8-32 screws.

- What advantage does a 4-in. octagon box have over a 3/4-in, octagon box?

Post Test

- What does a plan show about electrical cutlets?

- Electrical symbols used on an architectural plan show the location and type of electrical device required.

- What is an outlet?

- An electrical outlet is the source of electrical power you use to plug in many of your appliances, which is how you create that circuit in your home.

- Match the following switch types with the proper symbol

- single-pole S

- three-way S3

- four-way S4

- single-pole with pilot light Sp

- The plans show curved lines running between switches and various outlets. What do these lines Indicates?

- Switch leg; connects switched outlets with control points

- Why are the lines referred to in Question 4 usually curved?

- Curved lines are used to differentiate the electrical circuitry from the building construction drawing lines.

- What advantage does a 4-in octagon box have over a 314-in octagon box?

- The additional size will allow a greater number of conductors to enter and exit the box. The depth of the box can also be greater with a 4-in. octagon box than a 3 ¼-in.

- What is the size of the opening of a switch (device) box for a single device?

- The dimensions of a standard switch box is 2 in. x 3 in.

- The space between a door casing and a window casing is 312 in. (88.9 mm). Two switches are to be installed at this location. What type of switches wit be used?

- A piggy-back switch, which means the switches are stacked in the same area as a single switch. A standard 2-gang square box requires 4 inches so you can only use a single-gang box.

- Three switches are mounted in a 3-gang switch (device) box The wall plate for this assembly is called a three-ganged cover plate.

- The mounting holes in a device (switch) box are tapped for No. 6-32 screws. The mounting holes in an outlet box are tapped for No. 8-32 screws. The mounting holes in metal box attaching equipment grounding conductors are tapped for 10-32 screws.

- How high above the finished floor in the living room are switches located?

- 46 in.

- How high above the garage floor are switches located?

- 46in.

- How high above the finished floor in the living room are receptacles located?

- 12in

- How high above the garage floor are receptacles located?

- 46 in

- Outdoor receptacle outlets in this dwelling are located 18 in. above grade.

VII. SELF EVALUATION:

- What is the meaning of calculated load?

- Estimated load based on nominal values.

- How are branch circuits rated? See NEC 210.3

- Branch circuit rating is based on the overcurrent protection (breaker)

- How is the rating of the branch-circuit protective device affected when the conductors used are of a larger size than called for by the Code? See NEC 210.3.

- It is not affected. Rating of the branch circuit is determined by the overcurrent protection and not the conductor ampacity

- What dimensions are used when measuring the area of a building? See NEC 220.12.

- Dimensions form the occupied areas of the building.

- What spaces are not included in the floor area when computing the load in volt-amperes per square foot? See NEC 220.12.

- Open porches, garages, or other unfinished or unused spaces if they are not adaptable for future use.

Post Test

- According to NEC 210.50(C), a laundry equipment outlet must be placed within 6ft.  (1.8m) of the intended location of the laundry equipment.

- How is the total load in volt-amperes for lighting purposes determined? See NEC

- To find the general lighting load, the outside dimensions must be multiplied by a unit load of 3 volt-amperes per square foot. The minimum lighting load for this dwelling is 5,775 volt-amperes (55 x 35 x 3 = 5,775). With a voltage of 120/240, the general lighting load is 48 amperes (5,775 ÷ 120 = 48).

- How is the total lighting load in amperes determined?

- National Electrical Code considers a residence a listed occupancy at 3 VA per square foot; therefore, the general lighting load is determined by multiplying the square footage.

- How is the required number of branch circuits determined?

- The minimum number of branch circuits shall be determined from the total computed load and the size or rating of the circuits used.

- What is the minimum number of 15-ampere lighting branch circuits required if the dwelling has an occupied area of 4000 ft2 (368 m2)? Show all calculations.

- How many lighting branch circuits are provided in this dwelling?

-27

- What is the minimum load allowance for small-appliance circuits for dwellings?

-2

- An individual 15-ampere branch circuit is run to the receptacle outlet behind the refrigerator instead of connecting it to one of the two 20-ampere small-appliance branch circuits that are required in kitchens. For this separate circuit, an additional 1500 volt-amperes (shall) (does not have to) be added to the load calculations for dwellings. Circle the correct answer

- What is the smallest size wire that can be used in a branch circuit rated at 20 amperes?

- 12AWG

14. How is the load determined for outlets supplying specific appliances? See NEC 220.14.

- Considering a correction or derating factor of 80%

- What type of circuits must be provided for receptacle outlets in the kitchen, pantry, dining room, and breakfast room? See NEC 210.11(C)(1).

- General purpose circuits.

- How is the minimum number of receptacle outlets determined for most occupied rooms? NEC 210.52(A)

- No point on the wall more than 6ft from a receptacle.

- In a single-family dwelling, what types of overload protection for circuits are used? See NEC 240.6.

- Overcurrent protection (breaker) should be smaller than wire ampacity.